## Motor Load Schedule
Motor Load Schedule — Small Commercial Building
Motor ID | Equipment Description | Location | HP | Voltage (V) | Phase | FLA (A) NEC 430.250 | Service Factor | Duty | Notes
M-1 | Supply Fan (AHU-1) | Mechanical Room | 5 | 460 | 3 | 7.6 | 1.15 | Continuous
M-2 | Return Fan (AHU-1) | Mechanical Room | 3 | 460 | 3 | 4.8 | 1.15 | Continuous
M-3 | Chilled Water Pump (P-1) | Mechanical Room | 20 | 460 | 3 | 27 | 1.15 | Continuous
M-4 | Exhaust Fan (EF-1) | Roof | 1 | 460 | 3 | 2.1 | 1.15 | Continuous
M-5 | Cooling Tower Fan (CT-1) | Roof | 25 | 460 | 3 | 34 | 1.15 | Continuous
M-6 | Air Compressor (AC-1) | Mechanical Room | 15 | 460 | 3 | 21 | 1.15 | Continuous
Assumptions & sources:
• FLA values per NEC Table 430.250 (Full-Load Current, Three-Phase AC Motors), 460V column.
• Service factor of 1.15 assumed for standard NEMA-rated motors (verify against actual nameplate when equipment is selected).
• All loads assumed continuous duty per NEC Article 430.

## Cable Sizing
Cable Sizing — Based on NEC 430.22 (125%) and Table 310.16
NEC Table 310.16
Motor ID | Equipment Description | FLA (A) | Min. Conductor Ampacity (125%) | Selected Conductor (75°C Cu) | Selected Ampacity (A) | AWG Size | Ampacity (A) 75°C Cu
M-1 | Supply Fan (AHU-1) | 7.6 | 9.5 | 14 AWG | 20 | 1/0 AWG | 150
M-2 | Return Fan (AHU-1) | 4.8 | 6 | 14 AWG | 20 | 1 AWG | 130
M-3 | Chilled Water Pump (P-1) | 27 | 33.75 | 10 AWG | 35 | 2 AWG | 115
M-4 | Exhaust Fan (EF-1) | 2.1 | 2.625 | 14 AWG | 20 | 3 AWG | 100
M-5 | Cooling Tower Fan (CT-1) | 34 | 42.5 | 8 AWG | 50 | 4 AWG | 85
M-6 | Air Compressor (AC-1) | 21 | 26.25 | 10 AWG | 35 | 6 AWG | 65
[6 empty] | 8 AWG | 50
[6 empty] | 10 AWG | 35
[6 empty] | 12 AWG | 25
[6 empty] | 14 AWG | 20
Assumptions & sources:
• Minimum conductor ampacity = FLA x 1.25 per NEC 430.22 (continuous duty motor branch circuit).
• Conductor ampacities per NEC Table 310.16, copper conductors with 75°C terminations (THHN/THWN-2 assumed).
• Conduit fill, voltage drop, and ambient temperature derating not yet applied — covered later in the capstone.

## Panel Schedule
Panel Schedule — MCC Panel (Motors), Based on NEC 430.52
Standard breaker sizes
Circuit No. | Motor ID | Equipment Description | FLA (A) | Max Breaker (250% FLA) | Selected Breaker (A) | Poles | Phase | Conductor Size | Notes | Breaker (A)
1-3 | M-1 | Supply Fan (AHU-1) | 7.6 | 19 | 20 | 3 | A-B-C | 14 AWG |  | 250
4-6 | M-2 | Return Fan (AHU-1) | 4.8 | 12 | 15 | 3 | A-B-C | 14 AWG |  | 225
7-9 | M-3 | Chilled Water Pump (P-1) | 27 | 67.5 | 70 | 3 | A-B-C | 10 AWG |  | 200
10-12 | M-4 | Exhaust Fan (EF-1) | 2.1 | 5.25 | 15 | 3 | A-B-C | 14 AWG |  | 175
13-15 | M-5 | Cooling Tower Fan (CT-1) | 34 | 85 | 90 | 3 | A-B-C | 8 AWG |  | 150
16-18 | M-6 | Air Compressor (AC-1) | 21 | 52.5 | 60 | 3 | A-B-C | 10 AWG |  | 125
110
100
90
80
70
60
50
45
40
35
30
25
20
15
Assumptions & sources:
• Max breaker = FLA x 250% per NEC 430.52 (inverse-time circuit breaker, standard induction motor).
• Selected breaker rounds up to next standard size per NEC 430.52(C)(1) Exception No. 1.
• Circuit numbering is illustrative (sequential 3-pole groupings); confirm against actual panel schedule from panel manufacturer.
• All motors assumed on a dedicated 3-phase MCC panel — no other (lighting/receptacle) loads shown here.